## SummerSummary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Summer Summary: 2020-2024
Load Forecast, MW: |  | 2020 | 2021 | 2022 | 2023 | 2024
| Summer Peak Demand (based on normal weather) | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987
| plus: Energy Efficiency Program Savings Forecast, per Utilities Code Section 39.905 (b-4) | 1763.6799 | 2064.6831 | 2284.9232 | 2592.0334 | 2821.1604
| Total Summer Peak Demand (before Reductions from Energy Efficiency Programs) | 78459.2489 | 80363.3497 | 82392.5145 | 84185.2938 | 85803.2591
| less: Load Resources providing Responsive Reserves | -1173 | -1173 | -1173 | -1173 | -1173
| less: Load Resources providing Non-Spinning Reserves | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -786.0528 | -763.8576 | -763.8576 | -763.8576 | -763.8576
| less: TDSP Standard Offer Load Management Programs | -257 | -257 | -257 | -257 | -257
| less: Energy Efficiency Program Savings Forecast | -1763.6799 | -2064.6831 | -2284.9232 | -2592.0334 | -2821.1604
| Firm Peak Load, MW | 74479.5161 | 76104.809 | 77913.7337 | 79399.4027 | 80788.2411
Resources, MW: |  | 2020 | 2021 | 2022 | 2023 | 2024
| Installed Capacity, Thermal/Hydro | 65000.9413 | 65236.9413 | 65271.5413 | 65271.5413 | 65271.5413
| Switchable Capacity, MW | 3490 | 3490 | 3490 | 3490 | 3490
| less: Switchable Capacity Unavailable to ERCOT, MW | -842 | -542 | -542 | -542 | -542
| Available Mothballed Capacity, MW | 483 | 483 | 365 | 365 | 365
| Capacity from Private Use Networks | 3327.1496 | 3247.1496 | 3227.1496 | 3227.1496 | 2972.1496
| Coastal Wind, Peak Average Capacity Contribution (63% of installed capacity) | 1879.542 | 1879.542 | 1879.542 | 1879.542 | 1879.542
| Panhandle Wind, Peak Average Capacity Contribution (29% of installed capacity) | 1217.594 | 1221.074 | 1221.074 | 1221.074 | 1221.074
| Other Wind, Peak Average Capacity Contribution (16% of installed capacity) | 2496.128 | 2487.008 | 2487.008 | 2487.008 | 2487.008
| Solar Utility-Scale, Peak Average Capacity Contribution (76% of installed capacity) | 1648.7364 | 1648.7364 | 1648.7364 | 1648.7364 | 1648.7364
| Storage, Peak Average Capacity Contribution (0% of installed capacity) | 0 | 0 | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement, MW | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 78701.0913 | 79151.4513 | 79048.0513 | 79048.0513 | 78793.0513
| Non-Synchronous Ties, Capacity Contribution (68% of installed capacity) | 850 | 850 | 850 | 850 | 850
| Planned Resources (not wind, solar or storage) with Signed IA, Air Permits and Water Rights | 212 | 813 | 813 | 813 | 813
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (63% of installed capacity) | 661.311 | 1315.062 | 1315.062 | 1315.062 | 1315.062
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution (29% of installed capacity) | 134.27 | 449.732 | 580.957 | 652.877 | 652.877
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution (16% of installed capacity) | 652.368 | 1353.1056 | 1557.0736 | 1597.9216 | 1597.9216
| Planned Solar Utility-Scale, Peak Average Capacity Contribution (76% of installed capacity) | 1192.364 | 6034.78 | 7196.516 | 7196.516 | 7196.516
| Planned Storage, Peak Average Capacity Contribution (0% of installed capacity) | 0 | 0 | 0 | 0 | 0
| Total Capacity, MW | 82403.4043 | 89967.1309 | 91360.6599 | 91473.4279 | 91218.4279
| Reserve Margin | 0.10639 | 0.18215 | 0.17259 | 0.15207 | 0.12911
(Total Resources - Firm Load Forecast) / Firm Load Forecast

## SummerFuelTypes
Summer Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 63% for Coastal counties, 29% for Panhandle counties, and 16% for all other counties, while the solar capacity contribution is 76%. Private Use Network, and Hydro are included based on the three-year average historical capability for each Summer Season's 20 peak load hours. Non-Synchronous Tie resources import forecast is based on flows seen during Energy Emergency Alert (EEA) periods in the most recent summer of occurrence. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on a Seasonal Availability Schedule or Owner's reported Return Probability. Private Use Network is categorized as gas.
In MW
Fuel_Type | Capacity_Pct | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Biomass | 1 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
Coal | 1 | 14225 | 14225 | 14225 | 14225 | 14225 | 14225 | 14225 | 14225 | 14225 | 14225
Gas | 1 | 51846.1496 | 52903.1496 | 52799.7496 | 52799.7496 | 52544.7496 | 52544.7496 | 52544.7496 | 52544.7496 | 52544.7496 | 52544.7496
Nuclear | 1 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2
Other | 0.68 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850
Hydro | 0.82798 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413 | 457.5413
Wind-C | 0.63 | 2540.853 | 3194.604 | 3194.604 | 3194.604 | 3194.604 | 3194.604 | 3194.604 | 3194.604 | 3194.604 | 3194.604
Wind-P | 0.29 | 1351.864 | 1670.806 | 1802.031 | 1873.951 | 1873.951 | 1873.951 | 1873.951 | 1873.951 | 1873.951 | 1873.951
Wind-O | 0.16 | 3148.496 | 3840.1136 | 4044.0816 | 4084.9296 | 4084.9296 | 4084.9296 | 4084.9296 | 4084.9296 | 4084.9296 | 4084.9296
Solar | 0.76 | 2841.1004 | 7683.5164 | 8845.2524 | 8845.2524 | 8845.2524 | 8845.2524 | 8845.2524 | 8845.2524 | 8845.2524 | 8845.2524
Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 82403.4043 | 89967.1309 | 91360.6599 | 91473.4279 | 91218.4279 | 91218.4279 | 91218.4279 | 91218.4279 | 91218.4279 | 91218.4279
In Percentages
Fuel_Type |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Biomass |  | 0.0020533 | 0.0018807 | 0.001852 | 0.0018497 | 0.0018549 | 0.0018549 | 0.0018549 | 0.0018549 | 0.0018549 | 0.0018549
Coal |  | 0.17263 | 0.15811 | 0.1557 | 0.15551 | 0.15594 | 0.15594 | 0.15594 | 0.15594 | 0.15594 | 0.15594
Natural Gas |  | 0.62917 | 0.58803 | 0.57793 | 0.57721 | 0.57603 | 0.57603 | 0.57603 | 0.57603 | 0.57603 | 0.57603
Nuclear |  | 0.060352 | 0.055278 | 0.054435 | 0.054368 | 0.05452 | 0.05452 | 0.05452 | 0.05452 | 0.05452 | 0.05452
Other |  | 0.010315 | 0.0094479 | 0.0093038 | 0.0092923 | 0.0093183 | 0.0093183 | 0.0093183 | 0.0093183 | 0.0093183 | 0.0093183
Hydro |  | 0.0055525 | 0.0050856 | 0.0050081 | 0.0050019 | 0.0050159 | 0.0050159 | 0.0050159 | 0.0050159 | 0.0050159 | 0.0050159
Wind-C |  | 0.030834 | 0.035509 | 0.034967 | 0.034924 | 0.035021 | 0.035021 | 0.035021 | 0.035021 | 0.035021 | 0.035021
Wind-P |  | 0.016405 | 0.018571 | 0.019724 | 0.020486 | 0.020544 | 0.020544 | 0.020544 | 0.020544 | 0.020544 | 0.020544
Wind-O |  | 0.038208 | 0.042684 | 0.044265 | 0.044657 | 0.044782 | 0.044782 | 0.044782 | 0.044782 | 0.044782 | 0.044782
Solar |  | 0.034478 | 0.085404 | 0.096817 | 0.096698 | 0.096968 | 0.096968 | 0.096968 | 0.096968 | 0.096968 | 0.096968
Storage |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | bar: 2020 to 2029